## Hydrant1
HYDRANT FLOW TEST RESULTS
Location: |  |  |  |  | Demand Points
Date: |  |  |  |  | (l/min) | Disc (kPa)
Equipment:
Tested By:
Booster
Towns Main
Flow Rate (l/min) | " Hg | Discharge (kPa) | Suction (kPa) | Discharge (kPa) | Discharge (kPa) | Discharge (kPa) | Discharge (kPa) | Discharge (kPa)
Conclusion:
Comment:
BCA Design Requirement AS2419.1 (adopted in NSW after 1/1/92 NB transition time)
| Class | No Storeys |  | compartment flr area |  |  | L/s | L/Min
| 2,3,5 & 9 | 2 or less |  | =or< 1000m^2 |  | 1 outlet | 10 | 600
| 6,7 & 8 |  |  | =or< 500 m^2 |  | 1 outlet | 10 | 600
| 2,3,5 & 9 | 3 or more |  | >1000m^2 |  | 2 outlets | 20 | 1200
| all unsprinklered * |  |  | > 5000 m^2 |  | 3 outlets | 30 | 1800
| all sprinklered |  |  | >1000m^2 |  | 3 outlets | 30 | 1800
* add 1 additional outlet at 10L/s per 5000m^2
Ordinance 70 specification 10 prior to 1992
required at most disadvantaged hydrant 4.5 L/s through a 16mm nozzle at 275kPa
Fire Main required to be capable of handling:
| class 2,3,5 < 25m 11 L/s |  | class 2,3,5 > 25m 22 L/s
| class 6,7,8,9 >2 hydrants required 22L/s |  | class 6,7,8,9 <2 hydrants required 15L/s